## Table 4-Colo Gen
Year 2030
State of Colorado |  | Base |  |  |  | 3%
|  |  |  | Change |  |  |  | Change
Demand and Energy |  | Energy | 30% Energy | From 2012 |  | Energy | 30% Energy | From 2012
Forecast | MW | MWh | MWh | MW | MW | MWh | MWh | MW
| 13139 | 72726000 | 21818000 | 2926 | 17478 | 96799000 | 29040000 | 7108
Name Plate Calculations for
Wind Gen and Solar Gen
Wind Gen = 2/3 *30% of Energy |  |  | 14545333.3333 |  |  |  | 19360000
Solar Gen = 1/3 *30% of Energy |  |  | 7272666.6667 |  |  |  | 9680000
Wind Gen Demand at 37% load factor | 4487.6383 |  |  |  | 5973.0964
Solar Gen Demand | 1844.918 |  |  |  | 2455.6063
Photo voltaic is 25% of total, 30% load factor | 461.2295 |  |  |  | 613.9016
With Storage is 75% of total, 50% load factor | 1383.6885 |  |  |  | 1841.7047
On- peak and off-Peak Calculations
for Wind Gen and Solar Gen
Wind generation 20% on-peak | 897.5277 |  |  |  | 1194.6193
Wind generation 80% off-peak | 3590.1107 |  |  |  | 4778.4771
Solar generation
Photovoltaic 65% on-peak | 299.7992 |  |  |  | 399.036
With storage 95% on-peak | 1314.5041 |  |  |  | 1749.6195
Photovoltaic 0% off-peak | 0 |  |  |  | 0
With storage 0% off-peak | 0 |  |  |  | 0
Conventional Gen Required | 882.3291 |  |  |  | 4902.0052
including 16% reserves
IGD 03/21/2011 |  |  | Table 4

## Table 5-Base Allocation
Base Case Forecast
Heavy Summer
Inc. Generation for 2030
|  | Energy |  |  |  | Demand
|  | Fraction | Gs(PV) | Gs(CS) | Gw | Fraction | Gc | Total
Utility |  | of need | 300 | 1315 | 898 | of Need | 882
Black Hills |  | 0.046 | 13.8 | 60.49 | 41.308 | 0.0632 | 55.7424 | 171.4036
PSCo |  | 0.598 | 179.4 | 786.37 | 537.004 | 0.5127 | 452.2014 | 1955.4881
IREA |  | 0.017 | 5.1 | 22.355 | 15.266 |  | 0 | 42.721
CSU |  | 0.08 | 24 | 105.2 | 71.84 | 0.0815 | 71.883 | 273.0045
PRPA |  | 0.063 | 18.9 | 82.845 | 56.574 | 0.1053 | 92.8746 | 251.2989
T-S |  | 0.196 | 58.8 | 257.74 | 176.008 | 0.2373 | 209.2986 | 702.0839
| Total | 1 | 300 | 1315 | 898 |  | 882 | 3396
Off-peak -
50% of Heavy Summer
Inc. Generation for 2030
|  | Fraction | Gs(PV) | Gs(CS) | Gw |  | Gc | Total
Utility |  | of need | 0 | 0 | 3590 |  | 882
Black Hills |  | 0.046 | 0 | 0 | 165.14 |  | 55.7424 | 220.8824
PSCo |  | 0.598 | 0 | 0 | 2146.82 |  | 452.2014 | 2599.0214
IREA |  | 0.017 |  |  | 61.03 |  |  | 61.03
CSU |  | 0.08 | 0 | 0 | 287.2 |  | 71.883 | 359.083
PRPA |  | 0.063 | 0 | 0 | 226.17 |  | 92.8746 | 319.0446
T-S |  | 0.196 | 0 | 0 | 703.64 |  | 209.2986 | 912.9386
| Total |  | 0 | 0 | 3590 |  | 882 | 4472
IGD 3/21/2011 | [5 empty] | Table 5

## Table 6-3% Allocation
3% forecast
Heavy Summer
Inc. Generation for 2030
|  | Energy |  |  |  | Demand
|  | Fraction | Gs(PV) | Gs(CS) | Gw | Fraction | Gc | Total
Utility |  | of need | 399 | 1750 | 1195 | of Need | 4903
Black Hills |  | 0.041 | 16.359 | 71.75 | 48.995 | 0.0405 | 198.5715 | 335.716
PSCo |  | 0.63 | 251.37 | 1102.5 | 752.85 | 0.6388 | 3132.0364 | 5239.3952
IREA |  | 0.013 | 5.187 | 22.75 | 15.535 |  | 0 | 43.472
CSU |  | 0.081 | 32.319 | 141.75 | 96.795 | 0.0837 | 410.3811 | 681.3288
PRPA |  | 0.055 | 21.945 | 96.25 | 65.725 | 0.0665 | 326.0495 | 510.036
T-S |  | 0.18 | 71.82 | 315 | 215.1 | 0.1705 | 835.9615 | 1438.052
| Totals |  | 399 | 1750 | 1195 |  | 4903 | 8247
Off peak -
50% of Heavy Summer
Inc. Generation for 2030
|  | Fraction | Gs(PV) | Gs(CS) | Gw |  | Gc | Total
Utility |  | of need | 0 | 0 | 4778 |  | 4903
Black Hills |  | 0.041 | 0 | 0 | 195.898 |  | 198.5715 | 394.4695
PSCo |  | 0.63 | 0 | 0 | 3010.14 |  | 3132.0364 | 6142.1764
IREA |  | 0.013 |  |  | 62.114 |  | 0 | 62.114
CSU |  | 0.081 | 0 | 0 | 387.018 |  | 410.3811 | 797.3991
PRPA |  | 0.055 | 0 | 0 | 262.79 |  | 326.0495 | 588.8395
T-S |  | 0.18 | 0 | 0 | 860.04 |  | 835.9615 | 1696.0015
| Totals |  | 0 | 0 | 4778 |  | 4903 | 9681
IGD 03/21/2011 | [5 empty] | Table 6

## Table 7-conv Gen Allocation
Allocation of
Convectional
Generation
| Base |  | 3%
| MW |  | MW
PSCo
Pawnee-40% | 180.8 |  | 1252.8
Ft. St. Vrain-40% | 180.8 |  | 1252.8
RMEC-10% | 45.2 |  | 313.2
Spruce-10% | 45.2 |  | 313.2
Total | 452 |  | 3132
Black Hills
ERZ 5-100% | 56 |  | 199
Colo Spgs Utilities
Nixon-100% | 72 |  | 410
Platte River
Rawhide-100% | 93 |  | 326
Tri-State
Lamar-100% | 209 |  | 836
Total | 882 |  | 4903
IGD 03/21/2011 |  | Table 7